## ABIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK | [6 empty] | Transformer Axi-symmetric view
1 | 7.5 | 60 | 15.04 | 40 | 2 | 2 | 3.5
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6 | [6 empty] | Term. 2 |  | Term. 1
1=Y, 2=D, 3** | 2 | 1 | [8 empty] | Core Inner Dia = 15.04 |  | Lay. 1 |  | Lay. 2
MVA | 7.5 | 7.5 | [8 empty] | Core |  |  |  |  | Tank
kV | 65.55 | 12.47 | [10 empty] | 1.953 |  | 2.558
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6 |  |  |  |  | Lay. 1 inner dia. = 16.29
TERMINAL NR. | 2 | 1
INNER DIA | 16.29 | 22.57 | [8 empty] | Lay. 2 inner dia. = 22.57
RADIAL WIDTH | 1.953 | 2.558
LAST SEG | 3 | 6
NR. PARALL GR | 1 | 1 | [9 empty] | Z MIN | Z MAX
CURRENT +1/-1 | -1 | 1
CU = 1, AL = 2 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Z MIN | 3.19 | 17.35 | 21.07 | 3.25 | 17.35 | 21.07
Z MAX | 17.35 | 21.07 | 35.17 | 17.35 | 21.07 | 35.17
TOTAL TURNS | 74.4 | 8.1 | 74.1 | 714 | 156 | 714
ACTIVE TURNS | 74.4 | 8.1 | 74.1 | 714 | 0 | 714
STRANDS/TURN | 5 | 5 | 5 | 1 | 1 | 1
RAD STR NR/LAY. | 15 | 15 | 15 | 21 | 21 | 21
RAD STRAND DIM | 0.104 | 0.104 | 0.104 | 0.096 | 0.096 | 0.096
AX STRAND DIM | 0.384 | 0.384 | 0.384 | 0.25 | 0.25 | 0.25
Note on B3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used for Zbase Calculation
Note on H3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance from Outermost winding to Tank
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No. of parallel conductors per turn
Note on A25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total no. of radially placed conductors per disc
Note on A26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Thickness of conductor
Note on A27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Height of conductor

## ABMM
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK | [6 empty] | Transformer Axi-symmetric view
2 | 7.5 | 60 | 382.016 | 1016 | 2 | 2 | 88.9
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6 | [6 empty] | Term. 2 |  | Term. 1
1=Y, 2=D, 3** | 2 | 1 | [8 empty] | Core Inner Dia = 382.016 |  | Lay. 1 |  | Lay. 2
MVA | 7.5 | 7.5 | [8 empty] | Core |  |  |  |  | Tank
kV | 65.55 | 12.47 | [10 empty] | 49.6062 |  | 64.9732
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6 |  |  |  |  | Lay. 1 inner dia. = 413.766
TERMINAL NR. | 2 | 1
INNER DIA | 413.766 | 573.278 | [8 empty] | Lay. 2 inner dia. = 573.278
RADIAL WIDTH | 49.6062 | 64.9732
LAST SEG | 3 | 6
NR. PARALL GR | 1 | 1 | [9 empty] | Z MIN | Z MAX
CURRENT +1/-1 | -1 | 1
CU = 1, AL = 2 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Z MIN | 81.026 | 440.69 | 535.178 | 82.55 | 440.69 | 535.178
Z MAX | 440.69 | 535.178 | 893.318 | 440.69 | 535.178 | 893.318
TOTAL TURNS | 74.4 | 8.1 | 74.1 | 714 | 156 | 714
ACTIVE TURNS | 74.4 | 8.1 | 74.1 | 714 | 0 | 714
STRANDS/TURN | 5 | 5 | 5 | 1 | 1 | 1
RAD STR NR/LAY. | 15 | 15 | 15 | 21 | 21 | 21
RAD STRAND DIM | 2.6416 | 2.6416 | 2.6416 | 2.4384 | 2.4384 | 2.4384
AX STRAND DIM | 9.7536 | 9.7536 | 9.7536 | 6.35 | 6.35 | 6.35
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## CDIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 18 | 60 | 16.956 | 63.25 | 3 | 3 | 7.25
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 3 | 4 | 2
MVA | 18 | 18 | 0
kV | 115 | 34.5 | 13.8
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 3 | 2 | 1
INNER DIA | 18.383 | 23.98 | 31.18
RADIAL WIDTH | 0.4944 | 1.906 | 2.98
LAST SEG | 1 | 2 | 4
NR. PARALL GR | 1 | 1 | 2
CURRENT +1/-1 | -1 | 1 | -1
CU = 1, AL = 2 | 1 | 1 | 1 |  |  |  |  | Auto-transformer with unloaded tertiary winding
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Z MIN | 4 | 4 | 4 | 31.28
Z MAX | 57.46 | 57.46 | 30.17 | 57.45
TOTAL TURNS | 245.5 | 354 | 886.5 | 886.5
ACTIVE TURNS | 245.5 | 354 | 826.5 | 826.5
STRANDS/TURN | 1 | 3 | 1 | 1
RAD STR NR/LAY. | 3 | 15 | 22 | 22
RAD STRAND DIM | 0.14 | 0.1 | 0.099 | 0.099
AX STRAND DIM | 0.426 | 0.441 | 0.342 | 0.342
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## EFIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 5 | 60 | 13.782 | 50.125 | 3 | 3 | 3.5
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 5 | 6 | 2
MVA | 5 | 5 | 5
kV | 14.376 | 14.376 | 13.2
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 1 | 2 | 3
INNER DIA | 15.407 | 18.34 | 21.27
RADIAL WIDTH | 0.84 | 0.84 | 1.95
LAST SEG | 1 | 2 | 3
NR. PARALL GR | 1 | 1 | 1
CURRENT +1/-1 | -1 | -1 | 1
CU = 1, AL = 2 | 1 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Z MIN | 3 | 3 | 3
Z MAX | 45.3 | 45.3 | 45.3
TOTAL TURNS | 234 | 234 | 372
ACTIVE TURNS | 234 | 234 | 372
STRANDS/TURN | 2 | 2 | 3
RAD STR NR/LAY. | 6 | 6 | 15
RAD STRAND DIM | 0.116 | 0.116 | 0.106
AX STRAND DIM | 0.374 | 0.374 | 0.325
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## GHIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 30 | 60 | 20.68 | 69.5 | 2 | 2 | 4
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 1 | 2
MVA | 30 | 30
kV | 62.7 | 13.2
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 2 | 1
INNER DIA | 22.054 | 30.014
RADIAL WIDTH | 2.542 | 2.449
LAST SEG | 6 | 12
NR. PARALL GR | 1 | 2
CURRENT +1/-1 | -1 | 1
CU = 1, AL = 2 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Z MIN | 4.08 | 16.97 | 20.39 | 34.29 | 47.29 | 50.71 | 4.13 | 17.05 | 20.44 | 34.31 | 47.24 | 50.63
Z MAX | 16.97 | 20.39 | 33.39 | 47.29 | 50.71 | 63.6 | 17.05 | 20.44 | 33.36 | 47.24 | 50.63 | 63.55
TOTAL TURNS | 37.3 | 3.8 | 37.3 | 37.3 | 3.8 | 37.3 | 216 | 44 | 216 | 216 | 44 | 216
ACTIVE TURNS | 37.3 | 3.8 | 37.3 | 37.3 | 3.8 | 37.3 | 216 | 0 | 216 | 216 | 0 | 216
STRANDS/TURN | 17 | 17 | 17 | 17 | 17 | 17 | 2 | 2 | 2 | 2 | 2 | 2
RAD STR NR/LAY. | 27 | 27 | 27 | 27 | 27 | 27 | 22 | 22 | 22 | 22 | 22 | 22
RAD STRAND DIM | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082
AX STRAND DIM | 0.359 | 0.359 | 0.359 | 0.359 | 0.359 | 0.359 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## IJIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 20 | 60 | 18.916 | 72.5 | 2 | 3 | 3
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 2 | 1
MVA | 20 | 20
kV | 112.1 | 13.8
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 2 | 2 | 1
INNER DIA | 20.54 | 23.772 | 29.376
RADIAL WIDTH | 0.74 | 0.74 | 2.925
LAST SEG | 5 | 10 | 15
NR. PARALL GR | 1 | 1 | 1
CURRENT +1/-1 | -1 | -1 | 1
CU = 1, AL = 2 | 1 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Z MIN | 5.52 | 13.09 | 31.99 | 38.71 | 57.61 | 5.52 | 13.09 | 31.99 | 38.71 | 57.61 | 5.63 | 13.58 | 32.17 | 38.53 | 57.21
Z MAX | 13.09 | 31.99 | 38.71 | 57.61 | 65.18 | 13.09 | 31.99 | 38.71 | 57.61 | 65.18 | 13.58 | 32.17 | 38.53 | 57.21 | 65.08
TOTAL TURNS | 7 | 18.7 | 2.7 | 18.7 | 7 | 7 | 18.7 | 2.7 | 18.7 | 7 | 207 | 553 | 160 | 553 | 207
ACTIVE TURNS | 7 | 18.7 | 2.7 | 18.7 | 7 | 7 | 18.7 | 2.7 | 18.7 | 7 | 207 | 553 | 0 | 553 | 207
STRANDS/TURN | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 1 | 1 | 1 | 1 | 1
RAD STR NR/LAY. | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 20 | 20 | 20 | 20
RAD STRAND DIM | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.112 | 0.112 | 0.112 | 0.112 | 0.112
AX STRAND DIM | 0.424 | 0.424 | 0.424 | 0.424 | 0.424 | 0.424 | 0.424 | 0.424 | 0.424 | 0.424 | 0.352 | 0.352 | 0.352 | 0.352 | 0.352
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## KLIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 3.3 | 60 | 12.325 | 40.75 | 4 | 4 | 5
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 2 | 2 | 2 | 1
MVA | 1.65 | 1.65 | 1.65 | 1.65
kV | 34.5 | 34.5 | 0.55 | 0.55
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 3 | 4 | 1 | 2
INNER DIA | 15.33 | 15.33 | 22.39 | 22.39
RADIAL WIDTH | 1.96 | 1.96 | 2.6 | 2.6
LAST SEG | 1 | 2 | 3 | 4
NR. PARALL GR | 1 | 1 | 1 | 1 |  |  |  |  | IEEE CKT-31 Configuration
CURRENT +1/-1 | -1 | -1 | 1 | 1
CU = 1, AL = 2 | 1 | 1 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Z MIN | 3.65 | 21.75 | 3.5 | 21.625
Z MAX | 19.17 | 37.19 | 19.125 | 37.25
TOTAL TURNS | 19 | 11 | 1314 | 1314
ACTIVE TURNS | 19 | 11 | 1194 | 1194
STRANDS/TURN | 14 | 27 | 1 | 1
RAD STR NR/LAY. | 14 | 14 | 33 | 33
RAD STRAND DIM | 0.124 | 0.124 | 0.055 | 0.055
AX STRAND DIM | 0.417 | 0.372 | 0.257 | 0.257
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## MNIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 2.5 | 60 | 11.59 | 53 | 6 | 6 | 3
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 2 | 1 | 7 | 8 | 7 | 8
MVA | 1.25 | 1.25 | 1.25 | 1.25 | 1.25 | 1.25
kV | 0.48 | 0.48 | 13.187 | 2.173 | 13.187 | 2.173
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
INNER DIA | 12.88 | 12.88 | 18.63 | 24.18 | 18.63 | 24.18
RADIAL WIDTH | 1.55 | 1.55 | 1.762 | 0.12 | 1.762 | 0.12
LAST SEG | 1 | 2 | 3 | 4 | 5 | 6
NR. PARALL GR | 1 | 1 | 1 | 1 | 1 | 1
CURRENT +1/-1 | -1 | -1 | 1 | 1 | 1 | 1
CU = 1, AL = 2 | 1 | 1 | 1 | 1 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Z MIN | 3 | 28.5 | 3.5 | 3 | 29 | 28.75
Z MAX | 21 | 46.5 | 20.5 | 20.75 | 46 | 46.5
TOTAL TURNS | 19 | 11 | 551 | 86 | 551 | 86
ACTIVE TURNS | 19 | 11 | 522 | 86 | 522 | 86
STRANDS/TURN | 1 | 1 | 1 | 1 | 1 | 1
RAD STR NR/LAY. | 19 | 11 | 7 | 1 | 7 | 1
RAD STRAND DIM | 0.025 | 0.045 | 0.0907 | 0.0907 | 0.0907 | 0.0907
AX STRAND DIM | 10 | 10 | 0.1814 | 0.1814 | 0.1814 | 0.1814
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## OPIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 8.4 | 60 | 15.298 | 42.25 | 3 | 3 | 2.75
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 5 | 6 | 2
MVA | 8.4 | 8.4 | 8.4
kV | 7.558 | 7.558 | 34.5
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 1 | 2 | 3
INNER DIA | 17.74 | 21.54 | 24.84
RADIAL WIDTH | 1.03 | 1.03 | 3.21
LAST SEG | 1 | 2 | 4
NR. PARALL GR | 1 | 1 | 2
CURRENT +1/-1 | -1 | -1 | 1
CU = 1, AL = 2 | 1 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Z MIN | 3.44 | 3.44 | 3.5 | 20.54
Z MAX | 37.51 | 37.51 | 20.4 | 37.44
TOTAL TURNS | 81 | 81 | 640 | 640
ACTIVE TURNS | 81 | 81 | 640 | 640
STRANDS/TURN | 8 | 8 | 2 | 2
RAD STR NR/LAY. | 8 | 8 | 34 | 34
RAD STRAND DIM | 0.11 | 0.11 | 0.07 | 0.07
AX STRAND DIM | 0.292 | 0.292 | 0.253 | 0.253
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## QRIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 4.5 | 60 | 11.771 | 53 | 4 | 4 | 3
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 9 | 10 | 2 | 1
MVA | 4.5 | 4.5 | 2.25 | 2.25
kV | 26.4 | 5.195 | 2.2 | 2.2
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 4 | 3 | 2 | 1
INNER DIA | 13.097 | 13.097 | 18.8282 | 21.3198
RADIAL WIDTH | 1.8536 | 1.8536 | 0.6748 | 1.7325
LAST SEG | 1 | 2 | 4 | 6
NR. PARALL GR | 1 | 1 | 2 | 2
CURRENT +1/-1 | -1 | -1 | 1 | 1
CU = 1, AL = 2 | 1 | 1 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Z MIN | 1.25 | 24.421 | 1.31 | 24.685 | 1.3 | 24.766
Z MAX | 23.111 | 46.6688 | 23.06 | 46.435 | 22.675 | 46.141
TOTAL TURNS | 48 | 83 | 196 | 196 | 1062 | 1062
ACTIVE TURNS | 48 | 83 | 196 | 196 | 996 | 996
STRANDS/TURN | 9 | 5 | 1 | 1 | 1 | 1
RAD STR NR/LAY. | 10 | 10 | 2 | 2 | 22 | 22
RAD STRAND DIM | 0.11 | 0.11 | 0.12 | 0.12 | 0.055 | 0.055
AX STRAND DIM | 0.293 | 0.31 | 0.177 | 0.177 | 0.25 | 0.25
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.

## STIN
INPUT UNITS 1=inches 2=mm | BASE MVA | FREQUENCY | CORE DIAMETER | WINDOW HEIGHT | NUMBER OF TERMINALS | NUMBER OF LAYERS | DISTANCE TO TANK
1 | 10 | 60 | 15.3 | 51 | 3 | 3 | 4.75
TERMINAL NR. | 1 | 2 | 3 | 4 | 5 | 6
1=Y, 2=D, 3** | 2 | 1 | 1
MVA | 9.5 | 10 | 0.5
kV | 63.65 | 4.16 | 0.653 |  |  |  |  | Two winding Transformer with Regulated winding on LV.
LAYER NR. | 1 | 2 | 3 | 4 | 5 | 6
TERMINAL NR. | 3 | 2 | 1
INNER DIA | 16.714 | 19.106 | 25.006
RADIAL WIDTH | 0.27 | 1.928 | 2.476
LAST SEG | 1 | 2 | 3
NR. PARALL GR | 1 | 1 | 1
CURRENT +1/-1 | 1 | -1 | 1
CU = 1, AL = 2 | 1 | 1 | 1
SEGMENT NR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Z MIN | 4.75 | 3.87 | 3.88
Z MAX | 44.94 | 45.18 | 45.18
TOTAL TURNS | 16 | 51 | 1494
ACTIVE TURNS | 8 | 51 | 1350
STRANDS/TURN | 2 | 38 | 1
RAD STR NR/LAY. | 1 | 18 | 18
RAD STRAND DIM | 0.23 | 0.09 | 0.107
AX STRAND DIM | 0.5 | 0.284 | 0.32
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Documentation for additional type of Connections
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Auto or Phase Shifted windings, enter total MVA for both terminals.
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For Phase Shifted windings, enter Coil Voltage = No. of Turns x Volts/Turn. For all others, enter Line-Line voltage.